Facilities Management

DIRECTIVE NO. 797E	DATE: December 19, 2025

### SUBJECT: Management of Refrigerants

REFERENCES: Code of Federal Regulations (40 CFR 82 Subparts A to F and H, 40 CFR 84 Subpart C) and the general conditions of the University of Virginia’s Title V Permit.

PURPOSE: To establish a policy and procedure for managing refrigerants in compliance with the applicable federal regulations and to minimize emissions which contribute to ozone depletion and/or global warming.

CANCELLATION: This directive is effective immediately and supersedes and cancels Directive No. 797D, dated March 21, 2018; Subject: Refrigerant and Halon Management. Significant changes from the previous directive are printed in bold face type.

BACKGROUND: Many substances commonly used for refrigeration are classified as ozone depleting substances (ODS) or potent greenhouse gases. The U.S. EPA has developed regulations and implemented programs to phase out the production and use of ODS and phase down the production and use of hydrofluorocarbons (HFCs) in the United States. These regulations both require and prohibit certain procedures while performing service, maintenance, repair, or disposal of equipment containing refrigerant in order to minimize releases and maximize reclamation. Adequate recordkeeping is one of the most important aspects of demonstrating compliance.

POLICY: Facilities Management (FM) shall manage and control the use of refrigerant used in equipment it operates or maintains in accordance with regulatory requirements. This directive does not address refrigerant in motor vehicles; motor vehicle air conditioning systems should be serviced by an outside vendor or P&T.

## REVIEW DATE:

December 2028

## OFFICE OR DEPARTMENT RESPONSIBLE FOR REVIEW:

Environmental Resources

## PROCEDURES:

### Technician Training and Certification

  - Any person who could reasonably be expected to open a refrigerant circuit during maintenance, service, repair or disposal of equipment must pass a certification exam offered by an EPA-approved technician certification program. This is different from a journeyman or master tradesman license.

  - Apprentices are exempt from the requirement to be certified provided the apprentice is closely and continually supervised by a certified technician while performing any maintenance, service, repair, or disposal of refrigerant-containing equipment.

### Refrigerant Purchases

  - To improve tracking and accountability of our chemical inventory, each group below is encouraged to designate one primary and one alternate technician to be responsible for ordering refrigerant:

    - Chiller Plants

    - Each HSPP maintenance zone

    - Each Operations maintenance zone

### Supervisors or procurement staff must maintain refrigerant purchase records or be able to produce them from accounting software systems for five years.

- Refrigerant Storage and Inventory

  - Each group listed above shall designate specific refrigerant storage areas. The storage areas will be indoors, out of direct sunlight or freezing conditions. Where feasible, the storage areas will be conditioned spaces to minimize thermal expansion losses, and the storage area or cabinet will be lockable or otherwise secured to prevent unauthorized use of the refrigerant.

  - All new refrigerant not in immediate use and all reclaimed refrigerant will be stored in one of the designated storage areas until used or disposed/recycled.

  - Any addition or removal of refrigerant from a designated storage area can be tracked using Attachment 1, Refrigerant Storage Area Inventory Log, to ensure all material use is accounted for.

### Equipment Servicing

  - Only certified technicians will perform work on refrigerant circuits following the required practices pertaining to maintenance, service, repair, and disposal of such equipment.

  - EPA-approved methodology for minimizing loss and maximizing recovery of refrigerant shall be used. Intentional venting of ANY refrigerant into the atmosphere is prohibited while performing preventive maintenance, servicing, changing oil, repairing or disposing of equipment.

  - Prior to opening any refrigerant circuit, the technician must evacuate the refrigerant in either the entire unit or the part being serviced to a receiver within the system or to a certified recovery and/or recycling machine to prescribed vacuum levels. The technician must verify that the applicable level of evacuation has been reached before opening the equipment.

  - Follow EPA-required procedures to minimize the loss of refrigerant during oil changes.

- Requirements Applicable Only to Equipment ≥ 15 pounds of Refrigerant per Circuit

  - Technicians will complete a Refrigerant Use Form every time refrigerant is charged to or removed from a piece of equipment, even when not in response to a leak, and submit the form to the appropriate supervisor (Chiller Plants, HSPP or Operation Zones) within one business day of service and to the Refrigerant Compliance Manager within five business days of service. The Refrigerant Use Form is provided in Attachment 2. Refrigerant use will be tracked to the nearest pound, at a minimum.

  - The Refrigerant Compliance Manager will perform leak rate calculations using the annualizing leak rate method for equipment containing ≥ 15 pounds of refrigerant per circuit. If the equipment leak rate exceeds the regulatory thresholds, the appropriate manager whose personnel are responsible for servicing that unit will be informed. The allowable leak rates are:

    - 30% for industrial process refrigeration equipment,

    - 20% for commercial refrigeration equipment (i.e., retail food, cold storage), and

    - 10% for comfort cooling and other equipment.

  - Equipment found leaking refrigerant in excess of the regulatory thresholds, must be repaired or a retrofit/retirement plan prepared within 30 days of equipment exceeding the allowable leak rate. If needed, consult with the Refrigerant Compliance Manager to request an extension to the 30-day repair period. Mothballing equipment can extend the timelines.

  - An initial verification test must be performed to confirm the repairs stopped the leak. This test must be performed after completing the repairs and before adding refrigerant to the appliance and be performed within the 30-day repair period. If the initial verification test indicates that the repairs have not been successful, conduct additional repairs and initial verification tests as needed within the original 30-day repair period. Verification testing should be documented on the same Refrigerant Use Form filled out to document the original repair attempt.

  - A follow-up verification test must be performed within 10 days of the successful initial verification test or within 10 days of the equipment reaching normal operating characteristics and conditions. This test must demonstrate that the repairs stopped the leak. If the follow-up verification test indicates that the repairs have not been successful, conduct additional repairs and verification tests as needed within the original 30-day repair period. Verification testing should be documented on the same Refrigerant Use Form filled out to document the original repair attempt.

  - For equipment that exceeds the allowable leak rate and is not continuously monitored with an automatic leak detection system, a leak inspection must be conducted one year after the original repair attempt to verify the equipment is below the allowable leak rate. The inspection must be conducted by a certified technician using method(s) determined by the technician to be appropriate for the equipment. All visible and accessible components must be inspected. Leak inspections should be documented using the Leak Inspection Form provided in Attachment 3.

  - Automatic refrigerant leak detection systems used in lieu of leak inspections must be audited or calibrated annually. The Refrigerant Compliance Manager must be informed of each date the monitoring system identifies a leak and the location of the leak.

### Equipment Inventory

  - If any equipment containing ≥ 15 pounds of refrigerant is installed, removed or retrofit to use a different refrigerant, submit a completed Equipment Inventory Control Form (Attachment 4) to the Refrigerant Compliance Manager within one week of work completion.

  - The Refrigerant Compliance Manager will maintain a database with information on all equipment containing ≥ 15 pounds of refrigerant in an individual circuit. The inventory shall include the type of equipment (e.g., comfort cooling or commercial refrigeration), location, full charge capacity, the method used to determine the full charge and the installation date.

### Equipment Disposal or Resale

  - When disposing of equipment (regardless of the size), all refrigerant will be evacuated to the EPA-prescribed level prior to disposal and the amount recovered will be documented on the Refrigerant Use Form in Attachment 2 for equipment with ≥ 15 lbs./circuit and the Equipment Disposal Form in Attachment 5 for units with < 15 lbs./circuit. Recovered refrigerant will be stored in a designated storage area until sent off for recycling or destruction.

  - All equipment slated for disposal, including that taken to a landfill or scrap metal recycling business or placed in any dumpster including the metal recycling container, must be labeled using a sticker provided by the Refrigerant Compliance Manager to document that the refrigerant has been evacuated from the equipment.

  - Equipment turned over to Surplus does not need to be evacuated. Only equipment in good working order and not leaking refrigerant may go to Surplus.

### Refrigerant Recovery and/or Recycling Equipment

  - All recovery and/or recycling equipment used to evacuate refrigerant must be certified for the type of refrigerant and equipment. This equipment must be certified by an approved testing organization to meet EPA’s minimum requirements; a label to this effect should be on the equipment.

  - All recovery and/or recycling equipment shall be used and maintained in accordance with the manufacturer’s instructions. No person may alter the design of certified refrigerant recovery and/or recycling equipment in a way that would affect the equipment's ability to meet the certification standards.

### Waste Materials

  - Used refrigerant and used oil contaminated with refrigerant are not hazardous wastes if sent to a reclaimer.

  - Destruction of used refrigerant is an allowable disposal option.

### Spent refrigerant may not be sold or transferred for any other purpose than reclamation or destruction. Supervisors must maintain records of refrigerant sent off-site for these purposes for five years. These records should include the quantity of refrigerant by type transferred, the person to whom it was transferred, and the date of transfer.

  - Used refrigerant can be aggregated in recovery cylinders for bulk recycling. Different refrigerants should not be mixed in order to maximize the value of the reclaimed

refrigerant. To avoid cross contamination, use a grease/wax pencil, sticker or masking tape to note which type of refrigerant is in the recovery cylinder. Local vendors who will take reclaimed refrigerant include Aireco, Baker Distributing, Rapid Recovery, R.E. Michel, Southern Refrigeration and equipment manufacturers. Consult Environmental Health & Safety regarding protocols for satellite accumulation of spent or unwanted materials that exhibit hazardous characteristics such as ignitability.

### By 1/1/2028, once the technicians are finished using a disposable cylinder of an HFC, it must be sent to a reclaimer/recycler or refrigerant supplier for further processing to remove the heel. Alternatively, used disposable cylinders can be discarded if a certified technician removes the heel of the cylinder, evacuates the heel to a vacuum of 15 inches Hg, and provides a signed certification statement to the final processor which certifies that the heel was properly evacuated.

- Contracted Services

  - If hiring an outside contractor to install, service or dismantle FM operated or maintained equipment containing refrigerant, ensure that the contractor understands and follows the EPA-required practices. Prior to soliciting a quote, provide prospective contractors with the applicable regulatory requirements in Attachment 6. Include a copy of these requirements with the Request for Materials/Service form requesting use of an outside contractor.

  - Obtain documentation of the work performed from the contractor as specified in Attachment 6, Contractor Requirements.

## RESPONSIBILITIES:

### Chief Facilities Officer

Appoint a Refrigerant Compliance Manager, who will implement and administer the requirements of this directive.

### Department Directors (E&U, Operations, HSPP, CC&R)

Provide a copy of this directive to all affected employees within their department and ensure that all supervisory and other personnel in their department are aware of the responsibilities assigned to them by this directive.

### Refrigerant Compliance Manager

  - Serve as a resource to FM personnel regarding compliance with requirements pertaining to refrigerant.

  - Monitor changes in regulations concerning refrigerant and alert the Directors to pending changes in program requirements.

  - Conduct semiannual audits (at a minimum) of the refrigerant management system to ensure compliance with pertinent federal regulations and the University’s Title V Permit.

  - Maintain a database of all equipment containing ≥ 15 pounds of refrigerant per circuit.

  - Perform leak rate calculations and alert the appropriate supervisor of the need to conduct leak repair verification tests.

  - Schedule leak inspections in AiM as needed.

  - Submit annual report to EPA regarding chronically leaking equipment (≥ 125% of full charge in a calendar year) as needed.

  - Create equipment retrofit or retirement plans as necessary. Coordinate correspondence with EPA.

  - Maintain records of refrigerant use, disposal and leak rate calculations for a minimum of five years.

  - Conduct periodic refresher training to all employees responsible for refrigerant-containing equipment and associated technicians.

### Chiller Plants Manager and HVAC Supervisors

  - Develop and maintain a list of designated and secured refrigerant storage areas.

  - Ensure that refrigerant-containing equipment is repaired, replaced, converted or modified as necessary and in accordance with this directive.

  - Ensure that technicians working on refrigerant-containing equipment are certified by an EPA-approved certifying organization.

  - Ensure technicians are tracking refrigerant purchase, use and reclamation in accordance with this directive. Maintain refrigerant purchase and reclamation records for five years. Forward records of refrigerant use to the Refrigerant Compliance Manager within five business days of generation.

  - Ensure initial and follow-up leak rate verification tests and leak inspections are conducted in accordance with this directive and/or as requested by the Refrigerant Compliance Manager.

  - For any project that includes installation or removal of refrigerant-containing equipment, submit a completed Attachment 4 or 5, depending on the charge, to the Refrigerant Compliance Manager within one week of work completion. Ensure AiM records reflect the new and/or removed equipment.

  - Ensure contractors servicing or disposing of refrigerant-containing equipment are in compliance with regulatory requirements as summarized in Attachment 6.

### CC&R and C&RS Project Managers and Construction Administration Managers

  - For any project that includes servicing, repairing or removing equipment containing refrigerant, have the technician performing the work complete the appropriate Refrigerant Use Form and submit it to the Refrigerant Compliance Manager within five days of work completion.

  - Ensure contractors servicing or disposing of equipment containing refrigerant are in compliance with the requirements as summarized in Attachment 6.

  - For any project that includes installation or removal of refrigerant-containing equipment, submit a completed Attachment 4 or 5, depending on the charge, to the Refrigerant Compliance Manager within one week of work completion. Ensure AiM records reflect the new and/or removed equipment.

### Technicians

  - Technicians with an EPA certification must keep a copy of their certificate at their place of business. Save proof of certification to their Workday profile. Technicians must maintain a copy of their certificate until five years after no longer operating as a technician.

  - Provide a receipt or forward an electronic invoice to their supervisor for all purchases, disposal, and recycling of refrigerant.

  - Document the addition or removal of refrigerant to or from a designated storage area on the Refrigerant Storage Area Inventory Log, if used by their zone.

  - Follow the required practices pertaining to maintenance, service, repair, and disposal of equipment containing refrigerant. Verify that the applicable level of evacuation has been reached in refrigerant-containing equipment or the part before it is opened.

  - When refrigerant is added or removed from any FM operated or maintained equipment, even when not in response to a leak, submit a completed Refrigerant Use Form (Attachment 2) for equipment with ≥ 15 lbs./circuit or Equipment Disposal Form (Attachment 5) for equipment with < 15 lbs./circuit to their supervisor within one business day of service.

  - Document initial and follow-up verification tests for refrigerant containing equipment on the same Refrigerant Use Form documenting the original leak repair. Submit the form to their supervisor within one business day of conducting the tests.

  - Label evacuated equipment slated for disposal using a sticker noting the name of the person who recovered the refrigerant and the date the refrigerant was recovered. Alternately, note if all the refrigerant leaked out of the equipment prior to disposal.

### Surplus

  - Only accept refrigerant-containing equipment that is in good working order and not leaking refrigerant.

  - Any refrigerant-containing equipment that does not sell and is slated for disposal or recycling must have the refrigerant recovered and a corresponding Refrigerant Use Form completed and turned into the Refrigerant Compliance Manager within five business days.

Attachments:

- Refrigerant Storage Area Inventory Log

- Refrigerant Use Form (Equipment ≥ 15 lbs. per circuit)

- Leak Inspection Form (Equipment ≥ 15 lbs. per circuit)

- Equipment Inventory Control Form (Equipment ≥ 15 lbs. per circuit)

- Equipment Disposal Form (Equipment < 15 lbs. per circuit)

- Contractor Requirements

## DIRECTIVE 797E ATTACHMENT 1

Refrigerant Storage Area Inventory Log

# Refrigerant Storage Area Inventory Log

Month/Year:

Storage Area Name: 		Responsible Cost Center:

Starting Inventory:

| Refrigerant Type | Number of Cylinders | Total Weight (lbs.) |
| --- | --- | --- |

Activity Log:

| Date | Time | Technician Name | Refrigerant Type | Cylinder ID # | Cylinder Size | Cylinder Weight (lbs.) | Cylinder Status (circle one) |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | Added or Removed |
|  |  |  |  |  |  |  | Added or Removed |
|  |  |  |  |  |  |  | Added or Removed |
|  |  |  |  |  |  |  | Added or Removed |
|  |  |  |  |  |  |  | Added or Removed |
|  |  |  |  |  |  |  | Added or Removed |
|  |  |  |  |  |  |  | Added or Removed |
|  |  |  |  |  |  |  | Added or Removed |
|  |  |  |  |  |  |  | Added or Removed |
|  |  |  |  |  |  |  | Added or Removed |

Ending Inventory:

| Refrigerant Type | Number of Cylinders | Total Weight (lbs.) |
| --- | --- | --- |

## DIRECTIVE 797E ATTACHMENT 2

Refrigerant Use Form

(Equipment with ≥ 15 lbs./circuit)

## USE THIS FORM WHENEVER ANY REFRIGERANT IS ADDED TO OR REMOVED FROM ANY

MACHINE CONTAINING ≥ 15 LBS OF REFRIGERANT PER CIRCUIT

Submit this form within 1 business day of service to your Manager &

within 5 business days to the Refrigerant Compliance Manager (air@virginia.edu | 434-872-3548).

GENERAL INFORMATION

Building Name/ No.:

Work Order #:

AiM Asset #:

Equipment Name (manufacturer and circuit #):

DETAILS FOR SERVICE/REPAIR WORK & INITIAL VERIFICATION TEST

Date work performed (MM/DD/YY):

Work performed by (EPA certified technician):

Briefly describe the work performed: (i.e., part worked on and type of installation, service, repair or disposal performed)

Did you verify the applicable level of evacuation was reached before the machine was opened? YES or NO or N/A

Refrigerant Type:

Amount of NEW refrigerant added to equipment (lbs.): *If extracted refrigerant is returned to the circuit, do not record that as new refrigerant added.

Was this machine leaking refrigerant? YES or NO

Was the leak repaired (not just topped off)? YES or NO

How was the leak verified? Note the type of test used, test result and test date if different from repair date. *This must be done BEFORE adding refrigerant to leaking equipment.

If leak not repaired, what action will be taken? *Repairs must be made within 30 days. If not feasible, alert the Refrigerant Compliance Manager immediately.

Amount of refrigerant extracted for disposal (lbs.):

Refrigerant storage area:

DETAILS FOR LEAK RATE (To be completed by Refrigerant Compliance Manager)

Full charge of circuit (lbs.):

Leak rate by annualizing method (%):

Over allowable rate? YES or NO

A follow-up verification test must be performed within 10 days of the successful initial verification test OR within 10 days of the appliance reaching normal operating characteristics and conditions.

Only the part or system where a repair attempt was made needs to be tested. See first page of the form for details on the repair attempt.

DETAILS FOR FOLLOW-UP VERIFICATION TEST (To be completed by Technician performing test)

Date of follow-up test (MM/DD/YY):

Follow-up test performed by (EPA certified technician):

Was the leak repair successful? YES or NO

Which part of the system was tested?

Which method of testing was used to verify leak repair? ☐ Pressure/Vacuum Testing ☐ Electronic/Ultrasonic Leak Detectors ☐ Soap Bubbles ☐ Fluorescent Dye and Black Light ☐ Infrared/Near Infrared Testing ☐ Purge Runtime ☐ Handheld Gas Detection Device ☐ Other

Results of testing:

If repairs not successful, what action will be taken? *Repairs must be made within 30 days of original repair attempt

## DIRECTIVE 797E ATTACHMENT 3

### Leak Inspection Form

(Equipment with ≥ 15 lbs./circuit)

Submit this form to the Refrigerant Compliance Manager (air@virginia.edu | 424-872-3548). All visible and accessible components of the circuit must be inspected with the following exceptions:

- Where components are insulated, under ice that forms on the outside of equipment, underground, behind walls, or are otherwise inaccessible;

- Where personnel must be elevated more than two meters above a support surface; or

- Where components are unsafe to inspect, as determined by site personnel.

GENERAL INFORMATION

Building Name/ No.:

Work Order #:

AiM Asset #:

Equipment Name (manufacturer and circuit #):

DETAILS FOR LEAK INSPECTION

Which method of inspection was used to conduct the leak inspection? Check all that apply. Methods that determine the equipment is leaking refrigerant, but not the leak location: (Use with methods that determine leak location as necessary.) ☐ Standing pressure/vacuum decay tests ☐ Sight glass checks ☐ Viewing receiver levels ☐ Pressure checks ☐ Charging charts ☐ Purge Runtime ☐ Other: Methods that find refrigerant leak locations: ☐ Ultrasonic tests ☐ Gas-imaging cameras ☐ Bubble tests ☐ Leak detection device ☐ Other:

In the space below, list the location of each leak identified. If refrigerant is added to the circuit, document that on a Refrigerant Use Form. If the circuit is not leaking, state that.

I certify that all visible and accessible parts of the refrigerant circuit were inspected.

EPA Certified Technician Name: 		Date:

## DIRECTIVE 797E ATTACHMENT 4

Equipment Inventory Control Form

(Equipment with ≥ 15 lbs./circuit)

# Equipment Inventory Control Form

COMPLETE THIS FORM FOR UNITS CONTAINING ≥ 15 LBS OF REFRIGERANT PER CIRCUIT

## PLACED INTO SERVICE

Submit this form to the Refrigerant Compliance Manager (air@virginia.edu | 434-872-3548).

PLACED INTO SERVICE

AiM Asset ID:

Equipment Type* (check one): ☐ Comfort cooling & other non-industrial cooling or ☐ Commercial refrigeration

Machine (mnf, model #, serial #):

Equipment Location (bldg, room):

Area Served:

Cooling Capacity in Tons:

Refrigerant Type:

# of Circuits:

Full Charge (lbs./circuit):

How was full charge determined? (check one): ☐ Manufacturer’s data ☐ Calculated ☐ Measured ☐ Mid-point of estimated range**

Is it equipped with (check all that apply): ☐ Automatic leak detection system ☐ Purge ☐ Neither

Installation Date (MM/DD/YY):

Installer Name:

* Comfort cooling is used to control heat and/or humidity in occupied spaces. Commercial refrigeration is used for retail food and cold storage warehouse applications.

** If using a range, provide the range for the full charge and how the range was determined.

REMOVED FROM SERVICE

AiM Asset ID:

Machine (mnf, model #):

Equipment Location (bldg, room):

Refrigerant Type*:

* Extracted refrigerant should be documented on a Refrigerant Use Form

RETROFIT (refrigerant change)

AiM Asset ID:

Machine (mnf, model #):

Equipment Location (bldg, room):

Existing Refrigerant Type*:

New Refrigerant Type:

# of Circuits:

Full Charge (lbs./circuit):

* Extracted refrigerant should be documented on a Refrigerant Use Form

## DIRECTIVE 797E ATTACHMENT 5

Equipment Disposal Form (Equipment with < 15 lbs./circuit)

# Equipment Disposal Form

EQUIPMENT < 15 LBS OF REFRIGERANT PER CIRCUIT

Submit this form within 1 business day of service to your Manager &

within 5 business days to the Refrigerant Compliance Manager (air@virginia.edu | 434-872-3548).

| GENERAL INFORMATION |  |
| --- | --- |
| Building Name/ No.: |  |
| Equipment Location: |  |
| Equipment Name (manufacturer and circuit #): |  |
| Work Order #: |  |
| AiM Asset # (if available): |  |
| DETAILS FOR CIRCUIT EVACUATION |  |
| Date refrigerant recovered (MM/DD/YY): |  |
| Did all the refrigerant leak out of the equipment? | YES or NO |
| Was certified recover/recycling equipment used if the machine was opened? | YES or NO or N/A |
| Did you verify the applicable level of evacuation was reached before the machine was opened? | YES or NO or N/A |
| Refrigerant Type: |  |
| Amount of refrigerant recovered (lbs.): |  |
| Refrigerant storage area: |  |

Work Performed By	(Print):

(Signed):

EPA Certified Technician

## DIRECTIVE 797E ATTACHMENT 6

Contractor Requirements

# Refrigerant Contractor Requirements

- Only certified technicians will be allowed to maintain, service, repair, and dispose of equipment containing refrigerant. Technicians must keep a copy of their certificate at their place of business.

- All refrigerant recovery and/or recycling equipment must be certified by an approved equipment testing organization in accordance with 40 CFR 82 Subpart F on Refrigerant Recycling and Emissions Reduction.

- Technicians must follow the required practices pertaining to maintenance, service, repair, and disposal of refrigeration and air conditioning equipment provided in 40 CFR 82 Subpart F on Refrigerant Recycling and Emissions Reductions and 40 CFR 84 Subpart C on Management of Regulated Substances.

- For equipment containing 15 or more pounds of refrigerant per circuit, provide a written record documenting:

  - The identity and location of the equipment;

  - The date the work was performed and the name of the person performing the work;

  - The part(s) of the equipment being worked on;

  - The type of maintenance, service, repair or disposal performed for each part;

  - The amount and type of refrigerant added to or, in the case of disposal, removed from the equipment.

This record shall be provided to the UVA project manager or HVAC supervisor upon work completion. The attached form may be used for this recordkeeping requirement. [Provide the contractor with a copy of the Refrigerant Use Form in Attachment 2.]

- For disposal of equipment containing more than 5 and less than 15 pounds of refrigerant per circuit, provide a written record documenting:

  - The identity and location of the equipment;

  - The date of refrigerant recovery and the name of the person performing the work; and

  - The quantity and type of refrigerant recovered and to whom it was transferred for reclamation or disposal.

This record shall be provided to the UVA project manager or HVAC supervisor upon work completion. The attached form may be used for this recordkeeping requirement. [Provide the contractor with a copy of the Equipment Disposal Form in Attachment 5.]

- For disposal of small appliances, provide:

  - A signed statement or contract that all refrigerant that had not leaked previously has been recovered from the equipment. Include the date the refrigerant was recovered and the name and address of the person who recovered the refrigerant; or

  - A signed statement that all refrigerant had leaked out of the equipment and recovery was not possible.

This record shall be provided to the UVA project manager or HVAC supervisor upon work completion.